## SMA CP Fault Codes
Inverter Code | Manufacturer Description | LT Description | Potential Parts | Comments
1301 | Left-hand rotating magnetic field is connected.
1500 | AC Connection Issue | AC grid not stable |  | Check AC switch is on. Check frequency
3403 | PV array voltage is too high.
3404 | Open-circuit voltage is too high. Disturbance detected by standard monitoring
3406 | The DC voltage is too high.
3501 | The insulation monitoring device has measured a too low grounding resistance. | RISO error - below 1kOhm | Bender
3502 | The GFDI has tripped. | GFDI has tripped | GFDI
3504 | The insulation monitoring device has detected an insulation error.
3507 | A ground fault has occurred on the ungrounded terminal of the PV array.
3510 | The inverter has detected an insulation error on the inverter bridge.
3511
3512
3515
3517
3520
3601 | RISO error - below 45kOhm | RISO error - below 45kOhm | Bender
3803 | PV Array Current is too high | PV Array Current is too high
3803 | The PV array current is too high.
4003 | Reverse current detected | Reverse current detected
4003 | Reverse currents detected in the PV array or DC connection polarity reversed
6002
6113
6115
6116
6117
6119
6120 | Watchdog tripping error
6121 | No response from watchdog
6122 | Ten internal monitoring errors have occurred in succession.
6128 | General error
6404 | Overcurrent at L1, L2, L3 | Stack fault |  | Check SMA stack or Semikron - if Semikron check for 2-digit code on AST board
6405 | Overvoltage in the DC link of the inverter bridge
6410 | 24V supply voltage is invalid.
6417 | 15V supply voltage is invalid.
6418 | Overtemperature of the inverter bridge
6422 | Inverter bridge is in an undefined state | Inverter doesn't know which stack it has |  | Check stack parameters
6423 | Overtemperature in the switch cabinet |  | Choke
6425 | Synchronization error with utility grid |  | AC LEMs / Capacitors
6427 | Sensor error of DC voltage measurement
6440 | The HV transformer is no longer hermetically sealed |  | Check trafo parameters / check RIS on-site
6441 | Sensor error during measurement of DC Voltage
6443 | Unspecified error in digital signal processor
6447 | Self-test of inverter bridge failed
6448 | RISO device provides non-permitted values | RISO settings incorrect | Bender / cable between CAIO and Bender
6451 | Measured AC voltage of the inverter is less than utility grid voltage.
6452 | Measured AC voltage of the utility grid is less than inverter voltage.
6453 | AC voltage of grid limit monitoring is faulty.
6454 | AC current is faulty.
6455 | AC voltage is faulty.
6456 | Pre-charging circuit of DC link is defective.
6457 | Capacitor self test has failed |  | Capacitors (in stack cabinet) | can also be AC CTs
6461 | Insulation monitoring device has not adopted threshold.
6471 | Online capacitor self-test has failed.
6472 | Endless loop between online and offline capacitor test
6486 | Inadmissible deviations between AC power and DC power has been detected
6487 | AC ground fault has been detected.
6501 | Interior temperature of inverter is too high.
6502 | Temperature of inverter bridge is too high. |  | 3-phase fan / choke ?
6508 | Outside temperature is too high. | External temp sensor faulty | Temp sensor in roof
6512 | Minimum operating temperature not reached.
6605 | The fast stop was tripped due overtemperature in the switch cabinet.
7001 | Cable break or short circuit at inverter temperature sensor
7002 | Cable break or short circuit at inverter temperature sensor
7004 | Cable break or short circuit at inverter temperature sensor
7006 | Cable break or short circuit at inverter temperature sensor
7501 | Interior fan is defective | Interior fan is defective | LHS small fan - left
7502 | Interior fan is defective | Interior fan is defective | LHS small fan - right
7503 | Interior fan is defective | Interior fan is defective | 3-phase fan
7507 | Motor-protective circuit breaker of fan has tripped. | Interior fan is defective | Fan 3 in cabinet 2
7510 | Interior fan is defective | Interior fan is defective
7600 | Internal Comms Error |  | SC-COM/SC20CONT/SC20CAIO/display
7601 | Internal inverter error
7602 | Internal communication error has occurred or communication is interrupted.
7605 | Internal communication error has occurred or communication is interrupted. |  | SC20CAIO
7704 | Faulty switching status of DC switchgear | DC switch fault | Coils / DC Switch | Check which DC switch it is - EMax / TMax
7706 | Faulty switching status of the DC switchgear
7707 | Faulty switching status of AC disconnection unit | AC Contactor fault | AC Contactor / PCB
7708 | Faulty switching status of Remote GFDI | Remote GFDI | Remote GFDI Switch
7709 | 90% of switch cycles of the DC switchgear reached
7710 | 100% of switch cycles of the DC switchgear reached
7714 | Maximum number of GFDI switches reached | GFDI switch number high | Parameter / firmware | Check the number of switches - potential watchdog issue which a firmware update will cure
7801 | Surge arrester is defective | Surge arrester is defective | Surge arrester / connection cable | Check cable in bottom of surge protection
7901 | Reverse current has occurred in PV array
8004 | The inverter starts to derate due to overcurrent at the DC switchgear (SMID)
8701 | External active power setpoints are smaller than 2 mA and therefore invalid. The last valid value or, after a day change, Pmax is used. Once valid setpoints are available again, these will be used. | External active power setpoint
8702
8703
8704
9000 | Power electronics self-test is running. This message disappears once the self-test is complete.
9009 | Fast stop has tripped.
9013
9019 | Defective fast stop | Fast stop circuit needs checking |  | Check parameters and if a fast stop is installed, check that
0103 | Grid voltage is too high. Overvoltage detected by redundant monitoring.
0104 | Grid voltage is too high. Overvoltage detected by standard monitoring.
0203 | Grid voltage is too low. Undervoltage detected by redundant monitoring.
0204 | Grid voltage is too low. Undervoltage detected by standard monitoring.
0205 | Grid synchronization not possible
0404 | Frequency change per second too high for grid operation
0502
0503
0504
0505
0506
0801
0802