## Schneider GT Fault Codes
Inverter Code | Manufacturer Fault Source | Fault Type | Manufacturer Description | Possible Causes | LT Description | Potential Parts | Comments
1052 | Earth Fault |  | The PV array exceeds the differential current limit of the PV terminals
2052 | Under-voltage 24V Converter |  | The power semiconductors control voltage is below 20V
0010 | AC Frequency Low | Software |  | Utility grid frequency fell below the allowable limit
0011 | AC Frequency High | Software |  | Utility grid frequency rose above the allowable limit
0012 | AC Voltage Low | Software |  | AC Switch Micrologic
0013 | AC Voltage High | Software
0015 | Grid Disconnection | Software |  | AC Switch Micrologic
0016 | DC Disconnect Switch | Software |  | K31 is inoperable Q11 is inoperable
0017 | Phase Error | Software |  | Phase Rotation of the incoming grid connections is wrong
0018 | AC Contactor Circuit Fault | Software |  | K1 is inoperable K33 is inoperable | AC Contactor Fault | AC Contactor / auxiliary contact | Check aux cabling into contactor
0019 | PV Over-I Positive | Hardware |  | P3 on control unit is loose or disconnected PV system wiring short T13 is inoperable
0020 | PV Over-I Negative | Hardware |  | P3 on control unit is loose or disconnected PV system wiring short T14 is inoperable
0021 | PV Over Voltage | Software |  | Lightning strike on PV system wiring PV System Mis-wiring
0023 | Bus Voltage High | Software |  | Lightning strike on PV system wiring PV System Mis-wiring
0033 | Ground Over Current | Software |  | Fault between ground and live parts of the AC or DC system P3 on control unit is loose or disconnected
0035 | Fault Class 35 | Software | The Bender relay has detected a fault |  | RISO
0040 | Programming Software | Software | The system is in Programming mode
0041 | State Invalid | Software |  | CPU error Internal RAM error
0042 | Serial EEPROM Write Error | Software |  | CPU error Internal ROM error
0043 | Serial EEPROM Timeout | Software |  | CPU error Internal ROM error
0044 | Bad NOVRAM Memory | Software |  | CPU error Internal NOVRAM error
0045 | Interrupt 2 Timeout | Software |  | CPU error Internal A to D converter error
0047 | Software Test | Software | Software test fault has occurred
0048 | Bad Memory | Software |  | CPU error Internal SRAM error
0049 | Control Voltage Low | Software |  | Fuses F5, F6, F7 blown Units with optional ride-through: UPS is defective
0054 | Control Voltage High | Software |  | External control voltage source defective Units with optional ride-through: UPS is defective
0062 | Matrix Temperature | Hardware |  | Air flow on heat sink impeded due to accumulation of debris External cooling fan inoperable Operation above rated ambient temperature for an extended period of time
0072 | Local E-STOP | Software | Control unit has detected a loss of 15VDC at terminal J2-1 | Local E-STOP button is depressed
0073 | Remote E-STOP | Software | Control unit has detected a loss of 15VDC at terminal J2-5
0075 | Shutdown Remotely | Software |  | Remote Shutdown command via GUI
0082 | Matrix Not On | Software |  | FPGA inoperable Software acknowledge bit not accepted
0083 | Matrix Not Off | Software |  | FPGA inoperable Software acknowledge bit not accepted
0130 | Matrix Over Current - Phase A | Hardware |  | AC system wiring short P3 on control unit is loose or disconnected
0152 | IGBT Over Current |  | The current has exceeded 2000 Amps |  | Over current on AC side | AC CT (in power stage)
0153 | DC Over-current |  | DC Bus current has exceeded 1250A average
0230 | Matrix Over Current - Phase B | Hardware |  | AC system wiring short P3 on control unit is loose or disconnected
0252 | Switch Fault |  | An IGBT was activated, but no feedback signal was received confirming activation. There may be insufficient gate drive signal quality.
0430 | Matrix Over Current - Phase C | Hardware |  | AC system wiring short P3 on control unit is loose or disconnected
0452 | Over-temperature |  | AC Current converter's cooling element temperature has exceeded 80C. The temperature is displayed in the display.
0852 | Bus Voltage High | Hardware |  | Lightning strike on PV system wiring PV System Mis-wiring
0852 | Over-voltage DC Bus |  | The PV circuit voltage has exceeded 950V
0853 | Too Cold or Internal Voltage not in Range |  | The internal temperature sensor is reporting temp. below 0C. The internal control circuit supply voltage or clock have malfunctioned.
XX34 | Unused Matrix Over-I | Hardware | This fault indicates that the inverter has detected a control unit board failure | Problem on the control unit board